## Over view
Water Operators Report July 2022
Prepared by: Dave Shepherd
Water consumption
Monthly Consumption |  | 15728 | M3 | 28 | 561.7143 | M3 | Daily Average
Previous year 2021-01 |  | 24259 | M3 | 28 | 866.3929 | M3 | Daily Average
-35.17%
Vol Well #1 since 19 Jan 2019 |  | 224.96 | M3
Max Flow for month |  | 1691.8 | L/Min | Min Flow for month |  | 60.2 | L/Min (leak rate)
Time and Date |  | 30/07/2022 06:51 |  |  | 07/07/2022 16:37
Pump hours |  | # 2 | 671 | # 3 | 160 | #4 | 522
Previous month hrs |  |  | 414 |  | 6 |  | 268
VIHA Samples
Activity | Date | Location |  | Sample type | Result
Monthly | 11/07/2022 | 7941 Park |  | Drinking water | ü | Sent to VIHA
Sample /testing |  | 7588 Ships Pt. |  | Drinking water | ü
|  | 7576 Tozer |  | Drinking water | ü
|  | Well 2 |  | Raw | ü
|  | Well 3 |  | Raw | ü
|  | Well 4 |  | Raw | ü
Operations/Maintenance
Weekly:
Meter readings, CL residuals (5 locations) incl flushing station, run pump 1 collect well levels data
Check CL tank level and add accordingly
Monthly:
Prep chain of custody report and sample bottles Collect VIHA samples and deliver to office
Collect end of month Data create report, replace CL membrane, order chlorine as needed
Attend WTC and SPID Meetings
02/07/2022 | Create weekly consumption graph for water restriction stages
05/07/2022 | Comm's with Matt from Koflo re chlorine injection options obtain quote
$598 Quill no check valve with 3" stinger
$768 Quill no stinger with check valve
06/07/2022 | send MM idec info prep and attend AGM
07/07/2022 | Rick and I stripped down old #4 pump: intake was partially plugged which could explain poor
performance, rick will look into replacement seals and slip rings for a referb labour free and est
parts $500.00 Call out reset VFD re power bump
10/07/2022 | water shut off on SPR due to leak on property ask Nina to inform owner as not occupied
15/07/2022 | Comm's with Grant re Meet and great Denman Water
21/07/2022 | Open Pump house gate for BC Hydro contractor re access for work on neighbours property
25/07/2022 | Gen test, fault code under voltage! Checked all voltages and operations NFF
sent email to Cullen diesel re possible program parameters
28/07/2022 | Asist MM with datum levels Note normal demand close to 900 LPM at 5am!
30/07/2022 | MM and DS swap #2 and #4 sensors to confirm sensor in #4 okay, measure sensor heights for MM