## Over view
Water Operators Report June 2022
Prepared by: Dave Shepherd
Water consumption
Monthly Consumption |  | 7786 | M3 | 28 | 278.0714 | M3 | Daily Average
Previous year 2021-01 |  | 15492 | M3 | 28 | 553.2857 | M3 | Daily Average
-49.74%
Vol Well #1 since 19 Jan 2019 |  | 219.914 | M3
Max Flow for month |  | 2698.2 | L/Min | Min Flow for month |  | 28.3 | L/Min (leak rate)
Time and Date |  | 13/06/2022 11:16 |  |  | 11/06/2022 20:04
Pump hours |  | # 2 | 414 | # 3 | 6 | #4 | 268
Previous month hrs |  |  | 608 |  | 1 |  | 77
VIHA Samples
Activity | Date | Location |  | Sample type | Result
Monthly | 15/06/2022 | 7941 Park |  | Drinking water | ü | Sent to VIHA
Sample /testing |  | 7588 Ships Pt. |  | Drinking water | ü
|  | 7576 Tozer |  | Drinking water | ü
|  | Well 2 |  | Raw | ü
|  | Well 3 |  | Raw | ü
|  | Well 4 |  | Raw | ü
Operations/Maintenance
Weekly:
Meter readings, CL residuals (5 locations) incl flushing station, run pump 1 collect well levels data
Check CL tank level and add accordingly
Monthly:
Prep chain of custody report and sample bottles Collect VIHA samples and deliver to office
Collect end of month Data create report, replace CL membrane, order chlorine as needed
Attend WTC and SPID Meetings
07/06/2022 | Connect Dehumidifier as pipes sweating
11/06/2022 | Add De CL pucks to flushing station in prep for main line flushing
13/06/2022 | Main line flushing. Hydrant flushinf and valve exercise,
Call out re leak on SPR suspect hammer from flushing dug down to service box connection NFF
Leak 2' past at irrigation take off point not SPIDs responsibility
14/06/2022 | Main line flushing. Hydrant flushinf and valve exercise
Seach drawings and project photos re new hydro pole 7616 Tozer, print out and send to owner
15/06/2022 | Reseach Idec modual re #4 well level $430.00 (not sure I can do this as no visable addressing
17/06/2022 | Install new Generator control panel, Replacr P tube CL Pump # 1 switch to CL pump #2
18/06/2022 | Bump CL pump #2 up to 90% output from 57%
Call out low CL back flush quill
20/06/2022 | Monthly Generator test with John Lowe, Oil change, tested new panel by shutting of Hydro
22/06/2022 | AGM report
25/06/2022 | Low CL again back flush quill, switch CL pumps replave P tube #2
4pm Low CL alarm again! Check foot valve, test CL at pumphouse to ensure inhouse sensor working
Manual test aslo low! Swiths cl pumps and prime,
Call BT, DH & MM re quill replacement (thanks fr advice / help) called JA MF re shutown notice
Shut down all water pumps close input and output valves, remove quill and stem residual flow
with tap into quill location, Clean and replace quill slowley bring system up to pressure
Post Boil water advisory signs at Ships Point sign and SPID office, Monitor CL levels
26/06/2022 | Take CL residuals around point, (all above allowable) flushed mains at Flushing station with use of
main line valves to ensure direction of flow, retook CL residuals (all higher than 1st sample )
27/06/2022 | CL is fluctuating too much (average okay) switched on #2 pump to hand to minimize pump changes
this has helped and also taked the pressure off #4 draw down. Monitor CL…
29/06/2022 | Research Quill replacement aprox $683.00 USD
Mike and I discussing running 2 mixers in parallel to avoid future shutdowns re quill issues
Note on G9: Dave Shepherd: 25/06/2022 Flow 0 LPM 18:19-18:49 Due to System shut down